## Slide 1
Water Treatment
Topics: Water softening methods: - Lime-soda, Zeolite and ion exchange processes and their applications. Specifications of water for domestic use (ICMR and WHO); Unit processes involved in water treatment for municipal supply - Sedimentation with coagulant- Sand Filtration - chlorination; Domestic water purification – Candle filtration- activated carbon filtration; Disinfection methods - Ultrafiltration, UV treatment, Ozonolysis, Reverse Osmosis; Electro dialysis.
Module-2

## Slide 2: Water Softening methods
The process of removing the hardness producing substance from the water is called softening of water
In Industry three main methods are employed for softening of water
Lime soda process: lime Ca(OH)2 and soda Na2CO3 is added; (residual hardness: 15 to 60 ppm)
Zeolite (permutit) process: Hard water is filtered through a natural sand called the zeolite (residual hardness: up to10 ppm)
Ion-exchange and Mixed bed ion-exchange process:
Cation exchange resins (RH+)
Anion exchange resins (R’OH-)
Mixed bed ion-exchange

## Slide 3: Basic principles of Lime-soda process
In this process, all the soluble hardness-causing impurities are converted into insoluble precipitates which may be removed by setting and filtration
Lime [Ca(OH)2] and soda [Na2CO3] are the reagents used to precipitate the dissolved salts of Ca2+ and Mg2+ as CaCO3 and Mg(OH)2.
Reaction of Ca(HCO3)2 :
Ca(HCO3)2 + Ca(OH)2 2 CaCO3 + 2 H2O
Reaction of Mg(HCO3)2 :
Mg(HCO3)2 + 2 Ca(OH)2 2 CaCO3 + 2 H2O + Mg(OH)2
Lime removes the temporary hardness
Lime cannot remove the calcium permanent hardness which should be removed by soda

## Slide 4: Basic principles of Lime-soda process
a. Reaction of permanent calcium:
Ca2+ + Na2CO3 CaCO3 + 2Na+
b. Reactions of permanent magnesium:
Mg2+ + Ca(OH)2 Ca2+ + Mg(OH)2
Ca2+ + Na2CO3 CaCO3 + 2Na+
Lime cannot remove the calcium permanent hardness which should be removed by soda

## Slide 5
Lime Soda Process - Reactions of Lime and Soda
Ca(HCO3)2 + Ca(OH)2 → 2 CaCO3 ↓ + 2 H2O
Lime removes the temporary hardness:
Mg(HCO3)2 + 2 Ca(OH)2 → 2 CaCO3 ↓ + MgCO3 ↓ + 2 H2O
Soda and Lime removes the magnesium permanent hardness:
MgCl2 + Ca(OH)2 → CaCl2 + Mg(OH)2 ↓
CaCl2 + Na2CO3 → CaCO3 ↓ + 2 NaCl
MgSO4 + Ca(OH)2 → CaSO4 + Mg(OH)2 ↓
CaSO4 + Na2CO3 → CaCO3 ↓ + Na2SO4

## Slide 6
Soda removes all calcium permanent hardness:
CaCl2 + Na2CO3 → CaCO3 ↓ + 2 NaCl
CaSO4 + Na2CO3 → CaCO3 ↓ + Na2SO4
Reaction of CO2:
CO2 + Ca(OH)2 CaCO3 + H2O
Reaction of H+:
2 H+ + Ca(OH)2 Ca2+ + 2 H2O
Ca2+ + Na2CO3 CaCO3 + 2 Na+

## Slide 7
Working of Cold Lime –Soda Process

## Slide 8
Operated at room temperature.
Calculated amount of lime & soda mixed with water at room temperature with stirring.
Precipitate formed are finely formed hence do not settle down easily.
It is essential to add small amount of coagulant [aluminium sulphate, sodium aluminate, Alum (K2SO4·Al2(SO4)3·24H2O)]
Coagulant hydrolyse to form gelatinous precipitates and entraps the fine precipitate
The softened water passes through a filtering media (wood fibre) for complete removal of sludge
It provides water with a residual hardness of 50 to 60 ppm.
2 NaAlO2 + 4 H2O → Al(OH)3 ↓ + 2 NaOH
Al2(SO4)3 + 3 Ca(HCO3)2 → 3 CaSO4 + 2 Al(OH)3 + 6 CO2

## Slide 9
Reactions of coagulants:
a) Reaction of FeSO4:
Fe2+ + Ca(OH)2 Fe(OH)2 + Ca2+
Fe(OH)2 + H2O + O2 2 Fe(OH)3
Ca2+ + Na2CO3 CaCO3 + 2 Na
b) Reactions of Aluminium Sulphate (Al2(SO4)3 :
2 Al3+ + 3 Ca(OH)2 2 Al(OH)3 + 3 Ca2+
3 Ca2+ + 3 Na2CO3 3 CaCO3 + 6 Na+
c) Reactions of Sodium Aluminate (NaAlO2):
NaAlO2 + H2O Al(OH)3 + NaOH

## Slide 10
Hot lime-soda process consists of three parts:
Reaction tank to mix all ingredients
b) Conical sedimentation vessel where the sludge settles down
c) Sand filter where sludge is completely removed
Advantages of hot lime-soda process:
The precipitation reactions are almost complete.
Reactions takes place faster.
Sludge settles down rapidly; No coagulant is needed.
Dissolved gases (which may cause corrosion) are removed.
Viscosity of soft water is lower, hence filtered easily.
Residual hardness is low compared to cold lime-soda process.
Hot Lime –Soda Process

## Slide 11
Difference Between Soft and Hot lime soda Process
Cold lime-soda process | Hot lime-soda process
Done at room temp, 25 to 30°C. | Elevated temperature, 94 to 100°C
Slow Process | Rapid process
Use of Coagulants is must | Coagulants are not required
Filtration is not easy | Filtration is easy since the viscosity is low at high temperature
Residual hardness is around 60ppm | Residual hardness is 15-30ppm
Dissolved gases are not removed | Dissolved gases like O2 and CO2 removed to some extent
Low softening capacity | High softening capacity

## Slide 12: Advantages & disadvantages of lime-soda process:
Advantages of Lime – soda process:
Economical
Process improves the corrosion resistance of water.
Mineral content of water is reduced
The pH of water raises thus reducing content of pathogenic bacteria.
No skilled labour is required
Disadvantages of Lime – soda process:
Huge amount of sludge is formed and its disposal is difficult.
Due to residual hardness, water is not suitable for high pressure boilers.

## Slide 13
Lime[Ca(OH)2] required for softening
[ Temp. Ca2+ + 2×Temp. Mg2+ + Perm. (Mg2+ + Fe2+ + Al3+)
+ CO2 + H+ (HCl or H2SO4) + HCO3-] x Volume of water(V)
74
100
All components in CaCO3 equivalent
V = volume of water
Final result in mg >>> kg
100 parts by mass of CaCO3 ≡ 74 parts of Ca(OH)2
1 part of CaCO3 ≡ 74/100 of Lime
Soda [Na2CO3] required for softening
[ Perm. (Ca2+ + Mg2+ + Fe2+ + Al3+) + CO2 + H+ (HCl or
H2SO4) - HCO3-] x Volume of water (V)
106
100
100 parts by mass of CaCO3 ≡ 106 parts of Ca(OH)2
1 part of CaCO3 ≡ 106/100 of Lime