## Slide 1
Water Treatment
Topics: Water softening methods: - Lime-soda, Zeolite and ion exchange processes and their applications. Specifications of water for domestic use (ICMR and WHO); Unit processes involved in water treatment for municipal supply - Sedimentation with coagulant- Sand Filtration - chlorination; Domestic water purification – Candle filtration- activated carbon filtration; Disinfection methods - Ultrafiltration, UV treatment, Ozonolysis, Reverse Osmosis; Electro dialysis.
Module-2

## Slide 2: Water Softening methods
The process of removing the hardness producing substance from the water is called softening of water
In Industry three main methods are employed for softening of water
Lime soda process: lime Ca(OH)2 and soda Na2CO3 is added; (residual hardness: 15 to 60 ppm)
Zeolite (permutit) process: Hard water is filtered through a natural sand called the zeolite (residual hardness: up to10 ppm)
Ion-exchange and Mixed bed ion-exchange process:
Cation exchange resins (RH+)
Anion exchange resins (R’OH-)
Mixed bed ion-exchange

## Slide 3: Permutit or Zeolite Process
Zeolite is hydrated sodium aluminium silicate having a general formula, Na2OAl2O3.xSiO2.yH2O. (x=2 to 10 and y=2 to 6 )
It exchanges Na+ ions for Ca2+ and Mg2+ ions.
Common Zeolite is Na2OAl2O3.3SiO2.2H2O known as natrolith.
Other gluconites, green sand (iron potassium phyllosilicate with characteristic green colour, a mineral containing Glauconite)etc. are used for water softening.
Artificial zeolite used for water softening is Permutit.
These are porous, glassy particles having higher softening capacity compared to green sand.
They are prepared by heating china clay (hydrated aluminium silicate), feldspar (KAlSi3O8-NaAlSi3O8 – CaAl2Si2O8) are a group of rock-forming tectosilicate minerals which make up as much as 60% of the earth’s crust) and soda ash (Na2CO3)

## Slide 5
Types of zeolite
Natural Zeolites:
These are less porous, amorphous and durable
Natrolite: Na2O.Al2O3.4SiO2.2H2O
Laumontite: CaO. Al2O3.4SiO2.4H2O
Harmotome: (BaO.K2O).Al2O3.5SiO2.5H2O
They are capable of exchanging its Na ions.

## Slide 6: Zeolite process
Method of softening:
Na2Ze + Ca(HCO3)2 2 NaHCO3 + CaZe
Na2Ze + Mg(HCO3)2 2 NaHCO3 + MgZe
Na2Ze + CaSO4 2 Na2SO4 + CaZe
Na2Ze + CaCl2 2 NaCl + CaZe
For softening of water by zeolite process, hard water is percolated at a specified rate through a bed of zeolite, kept in a cylinder. Zeolite holds sodium ions loosely and can be represented as Na2Ze. Where Ze = insoluble radical frame work.
The hardness causing ions(Ca2+, Mg2+) are retained by the zeolite as CaZe and MgZe respectively, while the outgoing water contains sodium salts. During this process, the water becomes free from Ca2+ and Mg2+ ions.

## Slide 7: Zeolite Process Diagram

## Slide 8
Regeneration:
After some time, the zeolite is completely is completely converted into calcium and magnesium zeolite and it ceases to soften water, i.e., it gets exhausted.
At this stage, the supply of hard water is stopped and the exhausted zeolite is reclaimed by treating the bed with a concentrated (10%) brine (NaCl) solution.
The washing (containing CaCl2 and MgCl2 ) are led to drain and the regenerated zeolite bed thus-obtained is used again for softening purpose.
CaZe + 2 NaCl → CaCl2 + Na2Ze
MgZe + 2 NaCl → MgCl2 + Na2Ze
(Brine solution)

## Slide 9: Zeolites
Advantages:
  Residual hardness of water is about 10 ppm only
  Equipment is small and easy to handle
  Time required for softening of water is small
  No sludge formation and the process is clean
  Zeolite can be regenerated easily using brine solution
  Any type of hardness can be removed without any modifications to the process
Disadvantages:
  Coloured water or water containing suspended impurities cannot be used without filtration
  Water containing acidic pH cannot be used for softening since acid will destroy zeolite.